MODEL:JW-C350D400V  |1500rpm  |50Hz

| ESP StandbyPower | 330kVA | PRP PrimePower | 300kVA |
| --- | --- | --- | --- |
| ENGINE | DCECCummins | ALTERNATOR | STAMFORD |
|  | 6LTAA9.5-G1 |  | S4L1S-D41 |

GENERALFEATURES

| Engine:DCECCummins 6LTAA9.5-G1 | Alternator: singlebearing,IP23,insulationclassH |
| --- | --- |
| 50℃ radiator, fansaredrivenbybelt, withsafetyguard | Drytypeairfilter, fuelfilter&oilfilter |
| Vibration damper | Standard controlpanel |
| 24V chargingalternator | Exhaustbellows, elbows, flange &muffler |
| Lead-acidbatteries,rack and cables | Usermanual |

MODEL:JW-C350D400V  |1500rpm  |50Hz

GENERATORRATINGS

PF

（COSΦ)

StandbyAmps

StandbyRatings

(kW /kVA)

Voltage

Hz

Phase

PrimeRatings(kW /kVA)

| 440/254 | 50 | 3 | 0.8 | 433 | 264/330 | 240/300 |
| --- | --- | --- | --- | --- | --- | --- |
| 415/240 | 50 | 3 | 0.8 | 459 | 264/330 | 240/300 |
| 400/230 | 50 | 3 | 0.8 | 476 | 264/330 | 240/300 |
| 380/220 | 50 | 3 | 0.8 | 501 | 264/330 | 240/300 |

PrimePower (PRP):Prime power is available for anunlimitednumberofannualhoursinvariableloadapplication,inaccordancewithGB/T2820（eqvISO 8528）;A 10% overloadcapabilityisavailableforaperiodof1hourwithin  a12-hourperiodofoperation.

StandbyPowerRating(ESP):Thestandbypowerratingisapplicableforsupplyingemergencypowerforthedurationofautilitypowerinterruption.Nooverload,utilityparallelornegotiatedoutageoperationcapabilityisavailable atthisrating.

SALESPROMISES

JiweiPowerprovides a fullline of brandnew andhighqualityproducts.Eachandeveryunitis strictlyfactorytested.

Warrantyis according to our standard conditions:15months from thedateJIWEI sold tothefirstbuyeroroneyearafterinstallationor1000runninghours(accumulated),whichevercomesfirst.

Service andparts are available fromJiweiPower or distributorsinyourlocation.

MODEL:JW-C350D400V  |1500rpm  |50Hz

| ENGINESPECIFICATION |  |
| --- | --- |
| Manufacturer /Model | DCECCummins6LTAA9.5-G1 |
| Airintake system | Turbo, Air/Air cooling |
| Fuel system | fuelpump,EFC |
| Cylinder arrangement | 6inline |
| Displacement | 9.5L |
| Bore andstroke | 116.5*148(mm) |
| Compressionratio | 15.0 |
| Rated speed | 1500rpm |
| Max. Standbypower atratedspeed | 320KW/429HP |
| Governor type | Electronic |

| Exhaust System |  |
| --- | --- |
| Exhaust gas flow | 25kg/minm3/min |
| Exhaust temperature | 600℃ |
| Maxbackpressure | 10 |
| Air IntakeSystem |  |
| Maxintakerestriction | 6.2kPa |
| Combustion air flow | 18.6m3/min |
| Air flowrequired for radiator | 490m3/min |

MODEL:JW-C350D400V  |1500rpm  |50Hz

| Fuel System |  |  |
| --- | --- | --- |
| Fuelconsumption@100%(PrimePower)Load | 199g/kWh | 62.8L/h |
| Fuelconsumption@ 75%(PrimePower)Load | 196g/kWh | 46.5L/h |
| Fuelconsumption@ 50%(PrimePower)Load | 197g/kWh | 31.8L/h |

| OilSystem |  |
| --- | --- |
| Total oilcapacity | 32.4L |
| Oil consumption | ≤4g/kwh |
| Oil sumpcapacity | 32.4L |

| Cooling System |  |
| --- | --- |
| Coolant capacity | 11.1（仅发动机）L |
| Max water temperature | 104℃ |

MODEL:JW-C350D400V  |1500rpm  |50Hz

| ALTERNATORSPECIFICATION |  |
| --- | --- |
| IndustrialalternatorsmeettherequirementsoftherelevantpartsoftheBS5000, VDE0530,NEMAMG1-22,IEC34, CSA 22.2-100 andAS1359. |  |
| Alternator Data |  |
| Number ofPhase | 3 |
| Connecting Type | 3Phaseand 4 Wires, Ytypeconnecting |
| Number of Bearing | 1 |
| PowerFactor | 0.8 |
| Protection Class | IP23 |
| Altitude | ≤1000m |
| Exciter Type | Brushless exciting |
| InsulationClass/TemperatureRise | H/H |
| TelephoneInfluenceFactor(TIF) | ＜50 |
| THF | ＜2% |
| Alternator Capacity | 300kVA |
| Alternator Efficiency | 93.0% |

MODEL:JW-C350D400V  |1500rpm  |50Hz

| GENERATINGSETDATA |  |
| --- | --- |
| Relatedrange of voltage setting | ≥±5% |
| Steady-state voltage deviation | ≤±1% |
| Transientvoltagedeviation(100 % suddenpower decrease) | ≤+25% |
| Transient voltage deviation(suddenpowerincrease) | ≤-20% |
| Voltagerecoverytime (100% suddenpowerdecrease) | ≤6S |
| Voltagerecovery time (suddenpowerincrease) | ≤6S |
| Relatedrange of frequency setting | 0-5% adjustable |
| Steady-state frequencyband | ≤1.5% |
| Transientfrequencydeviation(100 % suddenpower decrease) | ≤+12% |
| Transient frequency deviation(suddenpowerincrease) | ≤-10% |
| Frequencyrecoverytime(100 % suddenpower decrease) | ≤5S |
| Frequencyrecovery time (suddenpowerincrease) | ≤5S |

| STANDARDFEATURES |  |  |
| --- | --- | --- |
| Standard auto controlsystem | Exhaust system(includinguntilmuffler) | Documents |
| Oil drainvalve | Startingbatteries (maintenance-free& watering-free) with connective wires | Special tools |
| Base fueltank | MCCB |  |

MODEL:JW-C350D400V  |1500rpm  |50Hz

| OPTIONS |  |  |
| --- | --- | --- |
| Daily fueltank | Rainproof type | Remote controlpanel |
| Alternator heater | Soundproof type | Paralleling system |
| Spareparts | Trailer type | Switchbox |
| Automatic transfer switch |  |  |

| DIMENSIONS&WEIGHT |  |
| --- | --- |
|  | Standard Configuration (open type withbasefueltank) |
|  | OverallDimensions: 2910×1100×1750mm |
|  | Weight: 2200kg |
|  | Soundproof Type |
|  | OverallDimensions: 3890×1460×2150mm |
|  | Weight: 3100kg |

Specifications are subject to changewithoutnotice.

Sichuan Jiweicheng Electric Power Equipment Co., LTD.

Website :www.scjiwei.com

Whatsapp/WeChat:+86 18981714166

https://scjiwei.en.alibaba.com

Email :jiwei166@scjiwei.com

Address: Building 7, Chengnan Tianfu Wisdom Garden, Pengshan District, Meishan City, Sichuan Province