MODEL: BF-C350XQ400V|1500rpm| 50Hz

| ESP StandbyPower | 330 kVA | PRP PrimePower | 300 kVA |
| --- | --- | --- | --- |
| ENGINE | Cummins | ALTERNATOR | STAMFORD |
|  | QSM11-G2 |  | S4L1D-D41 |

GENERAL FEATURES

| Engine: Cummins QSM11-G2 | Alternator: singlebearing,IP23,insulation classH |
| --- | --- |
| 40℃ radiator, fans are drivenbybelt,withsafetyguard | Dry type air filter, fuel filter&oil filter |
| Vibration damper | Standard controlpanel |
| 24V charging alternator | Exhaustbellows, elbows, flange &muffler |
| Lead-acidbatteries,rack and cables | Usermanual |

MODEL: BF-C350XQ400V|1500rpm| 50Hz

Hz

Voltage

PrimeRatings(kW /kVA)

PF

（COSΦ )

StandbyAmps

Phase

3 3

440/254

240/300

50

0.8

433

3

0.8

459

264/330

240/300

415/240

50

240/300

400/230

50

0.8

476

264/330

380/220

50

3

0.8

501

240/300

GENERATOR RATINGS

Standby Ratings (kW /kVA)

264/330 264/330

Prime Power (PRP): Prime power is available for an unlimited number of annual hoursin variableload application,in accordancewith GB/T2820（eqv ISO 8528）;A 10% overload capability is available for a period of 1 hourwithina12-hour period of operation.

StandbyPowerRating(ESP):Thestandbypowerratingisapplicableforsupplyingemergencypowerforthedurationofautilitypowerinterruption.Nooverload,utilityparallelornegotiatedoutageoperationcapabilityisavailable at thisrating.

SALESPROMISES

JiweiPower provides a fullline of brandnew andhighqualityproducts.Eachandeveryunitisstrictly factorytested.

Warrantyis according to our standard conditions:15months from the dateJIWEI sold tothefirstbuyeroroneyear after installation or1000runninghours (accumulated),whichever comes first.

Service andparts are available fromJiweiPower or distributors inyourlocation.

MODEL: BF-C350XQ400V|1500rpm| 50Hz

| ENGINE SPECIFICATION |  |
| --- | --- |
| Manufacturer /Model | Cummins QSM11-G2 |
| Air intakesystem | Turbocharged,intercooling |
| Fuel system | Celect |
| Cylinder arrangement | 6inline |
| Displacement | 10.8L |
| Bore andstroke | 125*147(mm) |
| Compression ratio | 16.2:1 |
| Rated speed | 1500rpm |
| Max. Standbypower atrated speed | 300KW |
| Governor type | Electronic |

| Exhaust System |  |
| --- | --- |
| Exhaust gas flow | 63.9m3/min |
| Exhaust temperature | 500℃ |
| Maxbackpressure | 10kPa |
| Air IntakeSystem |  |
| Maxintakerestriction | 6.2kPa |
| Combustion air flow | 26.16m3/min |
| Air flow required forradiator | 450m3/min |

MODEL: BF-C350XQ400V|1500rpm| 50Hz

| Fuel System |  |  |
| --- | --- | --- |
| Fuel consumption @100% (PrimePower)Load | 223g/kWh | 71L/h |
| Fuel consumption @ 75%(PrimePower)Load | 223g/kWh | 54L/h |
| Fuel consumption @ 50%(PrimePower)Load | 228g/kWh | 38L/h |

| Oil System |  |
| --- | --- |
| Total oilcapacity | 36.7L |
| Oil consumption | ≤4g/kwh |
| Oil sumpcapacity | 26-34L |

| Cooling System |  |
| --- | --- |
| Coolant capacity | 60L |
| Max water temperature | 104℃ |

MODEL: BF-C350XQ400V|1500rpm| 50Hz

| ALTERNATOR SPECIFICATION |  |
| --- | --- |
| Industrial alternatorsmeet therequirements of the relevantparts of theBS5000, VDE 0530,NEMA MG1-22,IEC34, CSA 22.2-100 andAS1359. |  |
| Alternator Data |  |
| Number ofPhase | 3 |
| Connecting Type | 3Phase and 4 Wires, Y type connecting |
| Number of Bearing | 1 |
| PowerFactor | 0.8 |
| Protection Class | IP23 |
| Altitude | ≤1000m |
| Exciter Type | Brushless exciting |
| Insulation Class/TemperatureRise | H/H |
| TelephoneInfluenceFactor (TIF) | ＜50 |
| THF | ＜2% |
| Alternator Capacity | 310kVA |
| Alternator Efficiency | 92.9% |

MODEL: BF-C350XQ400V|1500rpm| 50Hz

| GENERATING SET DATA |  |
| --- | --- |
| Relatedrange of voltage setting | ≥±5% |
| Steady-state voltage deviation | ≤±1% |
| Transient voltage deviation (100 %suddenpowerdecrease) | ≤+25% |
| Transient voltage deviation (suddenpowerincrease) | ≤-20% |
| Voltagerecovery time (100 %suddenpowerdecrease) | ≤6S |
| Voltagerecovery time (suddenpower increase) | ≤6S |
| Related range of frequency setting | 0-5% adjustable |
| Steady-state frequency band | ≤1.5% |
| Transient frequency deviation (100 %suddenpowerdecrease) | ≤+12% |
| Transient frequency deviation (suddenpowerincrease) | ≤-10% |
| Frequencyrecovery time (100 %suddenpowerdecrease) | ≤5S |
| Frequencyrecovery time (suddenpower increase) | ≤5S |

| STANDARD FEATURES |  |  |
| --- | --- | --- |
| Standard auto controlsystem | Exhaust system (includinguntilmuffler) | Documents |
| Oil drainvalve | Startingbatteries (maintenance-free & watering-free) with connective wires | Special tools |
| MCCB |  |  |

| MODEL: BF-C350XQ 400V¦ 1500rpm¦50Hz |  |  |  |
| --- | --- | --- | --- |
| OPTIONS |  |  |  |
| Daily fuel tank | Rainproof type |  | Remote controlpanel |
| Alternatorheater | Soundproof type |  | Paralleling system |
| Spareparts | Trailer type |  | Switchbox |
| Automatictransferswitch |  |  |  |

| DIMENSIONS & WEIGHT |  |
| --- | --- |
|  | Standard Configuration (open type) |
|  | OverallDimensions: 3000×1200×1800mm |
|  | Weight: 2420kg |
|  | Soundproof Type |
|  | OverallDimensions: 3890×1460×2150mm |
|  | Weight: 3770kg |

Specifications are subject to changewithout notice.

Sichuan Jiweicheng Electric Power Equipment Co., LTD.

Website :www.scjiwei.com

Whatsapp/WeChat:+86 18981714166

https://scjiwei.en.alibaba.com

Email :jiwei166@scjiwei.com

Address: Building 7, Chengnan Tianfu Wisdom Garden, Pengshan District, Meishan City, Sichuan Province