MODEL:JW-C375400V  |1500rpm  |50Hz

| ESP StandbyPower | 375kVA | PRP PrimePower | 344kVA |
| --- | --- | --- | --- |
| ENGINE | CCECCummins | ALTERNATOR | STAMFORD |
|  | NTA855-G2A |  | S4L1D-E41 |

GENERALFEATURES

| Engine: CCECCumminsNTA855-G2A | Alternator: singlebearing,IP23,insulationclassH |
| --- | --- |
| 40℃ radiator, fansaredrivenbybelt, withsafetyguard | Drytypeairfilter, fuelfilter&oilfilter |
| Vibration damper | Standard controlpanel |
| 24V chargingalternator | Exhaustbellows, elbows, flange &muffler |
| Lead-acidbatteries,rack and cables | Usermanual |

MODEL:JW-C375400V  |1500rpm  |50Hz

GENERATORRATINGS

PF

（COSΦ)

StandbyAmps

StandbyRatings

(kW /kVA)

Voltage

Hz

Phase

440/2545030.8                   492                    300/375                       275/344

415/240                5030.8                   529                    300/375                        275/344

400/230                5030.8                   541                    300/375                        275/344

380/2205030.8                   569300/375                        275/344

PrimeRatings(kW /kVA)

PrimePower (PRP):Prime power is available for anunlimitednumberofannualhoursinvariableloadapplication,inaccordancewithGB/T2820（eqvISO 8528）;A 10% overloadcapabilityisavailableforaperiodof1hourwithin  a12-hourperiodofoperation.

StandbyPowerRating(ESP):Thestandbypowerratingisapplicableforsupplyingemergencypowerforthedurationofautilitypowerinterruption.Nooverload,utilityparallelornegotiatedoutageoperationcapabilityisavailable atthisrating.

SALESPROMISES

JiweiPowerprovides a fullline of brandnew andhighqualityproducts.Eachandeveryunitis strictlyfactorytested.

Warrantyis according to our standard conditions:15months from thedateJIWEI sold tothefirstbuyeroroneyearafterinstallationor1000runninghours(accumulated),whichevercomesfirst.

Service andparts are available fromJiweiPower or distributorsinyourlocation.

MODEL:JW-C375400V  |1500rpm  |50Hz

| ENGINESPECIFICATION |  |
| --- | --- |
| Manufacturer /Model | CCECCumminsNTA855-G2A |
| Airintake system | Turbo, Water/Air cooling |
| Fuel system | PTtypefuelpump,EFC |
| Cylinder arrangement | 6inline |
| Displacement | 14L |
| Bore andstroke | 140*152（mm） |
| Compressionratio | 14.0:1 |
| Rated speed | 1500rpm |
| Max. Standbypower atratedspeed | 343KW/466HP |
| Governor type | Electronic |

| Exhaust System |  |
| --- | --- |
| Exhaust gas flow | 65.7m3/min |
| Exhaust temperature | 558℃ |
| Maxbackpressure | 10kPa |
| Air IntakeSystem |  |
| Maxintakerestriction | 6.25kPa |
| Combustion air flow | 24.06m3/min |
| Air flowrequired for radiator | 490.8m3/min |

MODEL:JW-C375400V  |1500rpm  |50Hz

| Fuel System |  |  |
| --- | --- | --- |
| Fuelconsumption@100%(PrimePower)Load | 191.3 g/kWh | 69.5L/h |
| Fuelconsumption@ 75%(PrimePower)Load | 194.9 g/kWh | 53.5L/h |
| Fuelconsumption@ 50%(PrimePower)Load | 207.1 g/kWh | 38.9L/h |

| OilSystem |  |
| --- | --- |
| Total oilcapacity | 38.6L |
| Oil consumption | ≤4g/kwh |
| Oil sumpcapacity | 28.4~36L |

| Cooling System |  |
| --- | --- |
| Coolant capacity | 85L |
| Max water temperature | 104℃ |

MODEL:JW-C375400V  |1500rpm  |50Hz

| ALTERNATORSPECIFICATION |  |
| --- | --- |
| IndustrialalternatorsmeettherequirementsoftherelevantpartsoftheBS5000, VDE0530,NEMAMG1-22,IEC34, CSA 22.2-100 andAS1359. |  |
| Alternator Data |  |
| Number ofPhase | 3 |
| Connecting Type | 3Phaseand 4 Wires, Ytypeconnecting |
| Number of Bearing | 1 |
| PowerFactor | 0.8 |
| Protection Class | IP23 |
| Altitude | ≤1000m |
| Exciter Type | Brushless exciting |
| InsulationClass/TemperatureRise | H/H |
| TelephoneInfluenceFactor(TIF) | ＜50 |
| THF | ＜2% |
| Alternator Capacity | 360kVA |
| Alternator Efficiency | 93.3% |

MODEL:JW-C375400V  |1500rpm  |50Hz

| GENERATINGSETDATA |  |
| --- | --- |
| Relatedrange of voltage setting | ≥±5% |
| Steady-state voltage deviation | ≤±1% |
| Transientvoltagedeviation(100 % suddenpower decrease) | ≤+25% |
| Transient voltage deviation(suddenpowerincrease) | ≤-20% |
| Voltagerecoverytime (100% suddenpowerdecrease) | ≤6S |
| Voltagerecovery time (suddenpowerincrease) | ≤6S |
| Relatedrange of frequency setting | 0-5% adjustable |
| Steady-state frequencyband | ≤1.5% |
| Transientfrequencydeviation(100 % suddenpower decrease) | ≤+12% |
| Transient frequency deviation(suddenpowerincrease) | ≤-10% |
| Frequencyrecoverytime(100 % suddenpower decrease) | ≤5S |
| Frequencyrecovery time (suddenpowerincrease) | ≤5S |

| STANDARDFEATURES |  |  |
| --- | --- | --- |
| Standard auto controlsystem | Exhaust system(includinguntilmuffler) | Documents |
| Oil drainvalve | Startingbatteries (maintenance-free& watering-free) with connective wires | Special tools |
| MCCB |  |  |

MODEL:JW-C375400V  |1500rpm  |50Hz

| OPTIONS |  |  |
| --- | --- | --- |
| Daily fueltank | Rainproof type | Remote controlpanel |
| Alternator heater | Soundproof type | Paralleling system |
| Spareparts | Trailer type | Switchbox |
| Automatic transfer switch |  |  |

| DIMENSIONS&WEIGHT |  |
| --- | --- |
|  | Standard Configuration (opentype) |
|  | OverallDimensions: 3100×1100×1900mm |
|  | Weight: 2870kg |
|  | Standard Configuration (withbase fuel tank) |
|  | OverallDimensions: 3100×1100×1900mm |
|  | Weight: 3000kg |
|  | Soundproof Type |
|  | OverallDimensions: 4230×1460×2150mm |
|  | Weight: 4330kg |

Specifications are subject to changewithoutnotice.

Sichuan Jiweicheng Electric Power Equipment Co., LTD.

Website :www.scjiwei.com

Whatsapp/WeChat:+86 18981714166

https://scjiwei.en.alibaba.com

Email :jiwei166@scjiwei.com

Address: Building 7, Chengnan Tianfu Wisdom Garden, Pengshan District, Meishan City, Sichuan Province