MODEL:JW-C440Q400V  |1500rpm  |50Hz

| ESP StandbyPower | 438kVA | PRP PrimePower | 400kVA |
| --- | --- | --- | --- |
| ENGINE | CCECCummins | ALTERNATOR | STAMFORD |
|  | QSNT-G3 |  | S4L1D-F41 |

GENERALFEATURES

| Engine: CCECCumminsQSNT-G3 | Alternator: singlebearing,IP23,insulationclassH |
| --- | --- |
| 40℃ radiator, fansaredrivenbybelt, withsafetyguard | Drytypeairfilter, fuelfilter&oilfilter |
| Vibration damper | Standard controlpanel |
| 24V chargingalternator | Exhaustbellows, elbows, flange &muffler |
| Lead-acidbatteries,rack and cables | Usermanual |

MODEL:JW-C440Q400V  |1500rpm  |50Hz

GENERATORRATINGS

PF

（COSΦ)

StandbyAmps

StandbyRatings

(kW /kVA)

Voltage

Hz

Phase

440/2545030.8                   575                    350/438                        320/400

415/240                5030.8                   609                    350/438                        320/400

400/230                5030.8                   632                    350/438                        320/400

380/2205030.8                   665350/438                        320/400

PrimeRatings(kW /kVA)

PrimePower (PRP):Prime power is available for anunlimitednumberofannualhoursinvariableloadapplication,inaccordancewithGB/T2820（eqvISO 8528）;A 10% overloadcapabilityisavailableforaperiodof1hourwithin  a12-hourperiodofoperation.

StandbyPowerRating(ESP):Thestandbypowerratingisapplicableforsupplyingemergencypowerforthedurationofautilitypowerinterruption.Nooverload,utilityparallelornegotiatedoutageoperationcapabilityisavailable atthisrating.

SALESPROMISES

JiweiPowerprovides a fullline of brandnew andhighqualityproducts.Eachandeveryunitis strictlyfactorytested.

Warrantyis according to our standard conditions:15months from thedateJIWEI sold tothefirstbuyeroroneyearafterinstallationor1000runninghours(accumulated),whichevercomesfirst.

Service andparts are available fromJiweiPower or distributorsinyourlocation.

MODEL:JW-C440Q400V  |1500rpm  |50Hz

| ENGINESPECIFICATION |  |
| --- | --- |
| Manufacturer /Model | CCECCumminsQSNT-G3 |
| Airintake system | Turbo,Air-Air cooling |
| Fuel system | CELECT |
| Cylinder arrangement | 6inline |
| Displacement | 14L |
| Bore andstroke | 140*152（mm） |
| Compressionratio | 16.7:1 |
| Rated speed | 1500rpm |
| Max. Standbypower atratedspeed | 392KW/525HP |
| Governor type | Electronic |

| Exhaust System |  |
| --- | --- |
| Exhaust gas flow | 2222kg/h |
| Exhaust temperature | 500℃ |
| Maxbackpressure | 10kpa |
| Air IntakeSystem |  |
| Maxintakerestriction | 6.2kPa |
| Combustion air flow | 30.66m3/min |
| Air flowrequired for radiator | 618m3/min |

MODEL:JW-C440Q400V  |1500rpm  |50Hz

| Fuel System |  |  |
| --- | --- | --- |
| Fuelconsumption@100%(PrimePower)Load | 205 g/kWh | 86.2L/h |
| Fuelconsumption@ 75%(PrimePower)Load | 213 g/kWh | 67.4L/h |
| Fuelconsumption@ 50%(PrimePower)Load | 226 g/kWh | 48.8L/h |

| OilSystem |  |
| --- | --- |
| Total oilcapacity | 38.6L |
| Oil consumption | ≤4g/kwh |
| Oil sumpcapacity | 28.4~36L |

| Cooling System |  |
| --- | --- |
| Coolant capacity | 85L |
| Max water temperature | 104℃ |

MODEL:JW-C440Q400V  |1500rpm  |50Hz

| ALTERNATORSPECIFICATION |  |
| --- | --- |
| IndustrialalternatorsmeettherequirementsoftherelevantpartsoftheBS5000, VDE0530,NEMAMG1-22,IEC34, CSA 22.2-100 andAS1359. |  |
| Alternator Data |  |
| Number ofPhase | 3 |
| Connecting Type | 3Phaseand 4 Wires, Ytypeconnecting |
| Number of Bearing | 1 |
| PowerFactor | 0.8 |
| Protection Class | IP23 |
| Altitude | ≤1000m |
| Exciter Type | Brushless exciting |
| InsulationClass/TemperatureRise | H/H |
| TelephoneInfluenceFactor(TIF) | ＜50 |
| THF | ＜2% |
| Alternator Capacity | 415kVA |
| Alternator Efficiency | 93.2% |

MODEL:JW-C440Q400V  |1500rpm  |50Hz

| GENERATINGSETDATA |  |
| --- | --- |
| Relatedrange of voltage setting | ≥±5% |
| Steady-state voltage deviation | ≤±1% |
| Transientvoltagedeviation(100 % suddenpower decrease) | ≤+20% |
| Transient voltage deviation(suddenpowerincrease) | ≤-15% |
| Voltagerecoverytime (100% suddenpowerdecrease) | ≤4S |
| Voltagerecovery time (suddenpowerincrease) | ≤4S |
| Relatedrange of frequency setting | 0-5% adjustable |
| Steady-state frequencyband | ≤0.5% |
| Transientfrequencydeviation(100 % suddenpower decrease) | ≤+10% |
| Transient frequency deviation(suddenpowerincrease) | ≤-7% |
| Frequencyrecoverytime(100 % suddenpower decrease) | ≤3S |
| Frequencyrecovery time (suddenpowerincrease) | ≤3S |

MODEL:JW-C440Q400V  |1500rpm  |50Hz

| OPTIONS |  |  |
| --- | --- | --- |
| Daily fueltank | Rainproof type | Remote controlpanel |
| Alternator heater | Soundproof type | Paralleling system |
| Spareparts | Trailer type | Switchbox |
| Automatic transfer switch |  |  |

| DIMENSIONS&WEIGHT |  |
| --- | --- |
|  | Standard Configuration (opentype) |
|  | OverallDimensions: 3300×1300×1900mm |
|  | Weight: 3200kg |
|  | Standard Configuration (withbase fuel tank) |
|  | OverallDimensions: 3300×1300×1900mm |
|  | Weight: 3350kg |
|  | Soundproof Type |
|  | OverallDimensions: 4630×1660×2250mm |
|  | Weight: 4620kg |

Specifications are subject to changewithoutnotice.

Sichuan Jiweicheng Electric Power Equipment Co., LTD.

Website :www.scjiwei.com

Whatsapp/WeChat:+86 18981714166

https://scjiwei.en.alibaba.com

Email :jiwei166@scjiwei.com

Address: Building 7, Chengnan Tianfu Wisdom Garden, Pengshan District, Meishan City, Sichuan Province