MODEL: JW-C1600400V|1500rpm| 50Hz

| ESP StandbyPower | 1650 kVA | PRP PrimePower | 1500 kVA |
| --- | --- | --- | --- |
| ENGINE | CCEC Cummins | ALTERNATOR | STAMFORD |
|  | KTA50-GS8 |  | S7L1D-C4 |

GENERAL FEATURES

| Engine: CCEC CumminsKTA50-GS8 | Alternator: singlebearing,IP23,insulation classH |
| --- | --- |
| 40℃ radiator, fans are drivenbybelt, withsafetyguard | Dry type air filter, fuel filter &oilfilter |
| Vibration damper | Standard controlpanel |
| 24V charging alternator | Exhaustbellows, elbows, flange &muffler |
| Lead-acidbatteries,rack and cables | Usermanual |

MODEL: JW-C1600400V|1500rpm| 50Hz

Voltage

StandbyRatings

(kW /kVA)

PrimeRatings(kW /kVA)

Phase

PF

（COSΦ )

StandbyAmps

440/254

1320/1650

1200/1500

3

0.8

2165

2295

3

50

415/240

0.8

1320/1650

1200/1500

1200/1500

400/230

1320/1650

0.8

3

2381

380/220

50

3

0.8

2506

1320/1650

1200/1500

GENERATOR RATINGS

Hz

50 50

Prime Power (PRP): Prime power is available for an unlimited number of annual hoursin variableload application,in accordancewith GB/T2820（eqv ISO 8528）;A 10% overload capability is available for a period of 1 hourwithina12-hour period of operation.

StandbyPowerRating(ESP):Thestandbypowerratingisapplicableforsupplyingemergencypowerforthedurationofautilitypowerinterruption.Nooverload,utilityparallelornegotiatedoutageoperationcapabilityisavailable at thisrating.

SALESPROMISES

JiweiPower provides a fullline of brandnew andhighqualityproducts.Eachandeveryunitisstrictly factorytested.

Warrantyis according to our standard conditions:15months from the dateJIWEI sold tothefirstbuyeroroneyear after installation or1000runninghours (accumulated),whichever comes first.

Service andparts are available fromJiweiPower or distributors inyourlocation.

MODEL: JW-C1600400V|1500rpm| 50Hz

| ENGINE SPECIFICATION |  |
| --- | --- |
| Manufacturer /Model | CCEC CumminsKTA50-GS8 |
| Air intakesystem | Turbo,Air/Water cooling |
| Fuel system | PT type fuelpump,EFC |
| Cylinder arrangement | 16in“V” |
| Displacement | 50.3L |
| Bore andstroke | 159*159（mm） |
| Compression ratio | 14.9:1 |
| Rated speed | 1500rpm |
| Max. Standbypower atrated speed | 1429KW/1944HP |
| Governor type | Electronic |

| Exhaust System |  |
| --- | --- |
| Exhaust gas flow | 261m3/min |
| Exhaust temperature | 510℃ |
| Maxbackpressure | 7kPa |
| Air IntakeSystem |  |
| Maxintakerestriction | 6.23kPa |
| Combustion air flow | 99.3m3/min |
| Air flow required forradiator | 1680m3/min |

MODEL: JW-C1600400V|1500rpm| 50Hz

| Fuel System |  |  |
| --- | --- | --- |
| Fuel consumption @100% (PrimePower)Load | 204 g/kWh | 313L/h |
| Fuel consumption @ 75%(PrimePower)Load | 210 g/kWh | 243L/h |
| Fuel consumption @ 50%(PrimePower)Load | 221 g/kWh | 175L/h |

| Oil System |  |
| --- | --- |
| Total oilcapacity | 204L |
| Oil consumption | ≤4g/kwh |
| Oil sumpcapacity | 148~178L |

| Cooling System |  |
| --- | --- |
| Coolant capacity | 380L |
| Max water temperature | 104℃ |

MODEL: JW-C1600400V|1500rpm| 50Hz

| ALTERNATOR SPECIFICATION |  |
| --- | --- |
| Industrial alternatorsmeet therequirements of the relevantparts of theBS5000, VDE 0530,NEMA MG1-22,IEC34, CSA 22.2-100 andAS1359. |  |
| Alternator Data |  |
| Number ofPhase | 3 |
| Connecting Type | 3Phase and 4 Wires, Y type connecting |
| Number of Bearing | 1 |
| PowerFactor | 0.8 |
| Protection Class | IP23 |
| Altitude | ≤1000m |
| Exciter Type | Brushless exciting |
| Insulation Class/TemperatureRise | H/H |
| TelephoneInfluenceFactor (TIF) | ＜50 |
| THF | ＜2% |
| Alternator Capacity | 1550kVA |
| Alternator Efficiency | 95.4% |

MODEL: JW-C1600400V|1500rpm| 50Hz

| GENERATING SET DATA |  |
| --- | --- |
| Relatedrange of voltage setting | ≥±5% |
| Steady-state voltage deviation | ≤±1% |
| Transient voltage deviation (100 %suddenpowerdecrease) | ≤+25% |
| Transient voltage deviation (suddenpowerincrease) | ≤-20% |
| Voltagerecovery time (100 %suddenpowerdecrease) | ≤6S |
| Voltagerecovery time (suddenpower increase) | ≤6S |
| Relatedrange of frequency setting | 0-5% adjustable |
| Steady-state frequency band | ≤1.5% |
| Transient frequency deviation (100 %suddenpowerdecrease) | ≤+12% |
| Transient frequency deviation (suddenpowerincrease) | ≤-10% |
| Frequencyrecovery time (100 %suddenpowerdecrease) | ≤5S |
| Frequencyrecovery time (suddenpower increase) | ≤5S |

| STANDARD FEATURES |  |  |
| --- | --- | --- |
| Standard auto controlsystem | Exhaust system (includinguntilmuffler) | Documents |
| Oil drainvalve | Startingbatteries (maintenance-free & watering-free) with connective wires | Special tools |

| MODEL: JW-C1600 400V¦ 1500rpm¦50Hz |  |  |  |
| --- | --- | --- | --- |
| OPTIONS |  |  |  |
| Daily fuel tank | Rainproof type |  | Remote controlpanel |
| Alternatorheater | Soundproof type |  | Paralleling system |
| Spareparts | Trailer type |  | Switchbox |
| Automatictransferswitch |  |  |  |

| DIMENSIONS & WEIGHT |  |
| --- | --- |
|  | Standard Configuration (open type) |
|  | OverallDimensions: 5550×2150×2550mm |
|  | Weight:11000kg |
|  | Soundproof Type (standard 20’ftHQ container) |
|  | OverallDimensions: 6058×2438×2896mm |
|  | Weight:16000kg |

Specifications are subject to changewithout notice.

Sichuan Jiweicheng Electric Power Equipment Co., LTD.

Website :www.scjiwei.com

Whatsapp/WeChat:+86 18981714166

https://scjiwei.en.alibaba.com

Email :jiwei166@scjiwei.com

Address: Building 7, Chengnan Tianfu Wisdom Garden, Pengshan District, Meishan City, Sichuan Province