MODEL:JW-C1875400V  |1500rpm  |50Hz

| ESP StandbyPower | 1875kVA | PRP PrimePower | N/A |
| --- | --- | --- | --- |
| ENGINE | CCECCummins | ALTERNATOR | STAMFORD |
|  | KTA50-G15 |  | PI734ES1 |

GENERALFEATURES

| Engine: CCECCumminsKTA50-G15 | Alternator: singlebearing,IP23,insulationclassH |
| --- | --- |
| 40℃ radiator, fansaredrivenbybelt, withsafetyguard | Drytypeairfilter, fuelfilter&oilfilter |
| Vibration damper | Standard controlpanel |
| 24V chargingalternator | Exhaustbellows, elbows, flange &muffler |
| Lead-acidbatteries,rack and cables | Usermanual |

MODEL:JW-C1875400V  |1500rpm  |50Hz

GENERATORRATINGS

StandbyAmps

StandbyRatings

(kW /kVA)

PF

（COSΦ)

Voltage

Hz

Phase

440/254               50                30.8                  2460                 1440/1800                         N/A

415/240               50                30.8                  2609                 1440/1800                         N/A

400/230               50                30.8                  2706                 1440/1800                         N/A

380/220               50                3                  0.8                  2849                 1440/1800                         N/A

PrimeRatings(kW /kVA)

PrimePower (PRP):Prime power is available for anunlimitednumberofannualhoursinvariableloadapplication,inaccordancewithGB/T2820（eqvISO 8528）;A 10% overloadcapabilityisavailableforaperiodof1hourwithin  a12-hourperiodofoperation.

StandbyPowerRating(ESP):Thestandbypowerratingisapplicableforsupplyingemergencypowerforthedurationofautilitypowerinterruption.Nooverload,utilityparallelornegotiatedoutageoperationcapabilityisavailable atthisrating.

SALESPROMISES

BaifaPowerprovides a fullline of brandnew andhighqualityproducts.Eachandeveryunitis strictlyfactorytested.

Warrantyis according to our standard conditions:15months from thedateBAIFA sold tothefirstbuyeroroneyearafterinstallationor1000runninghours(accumulated),whichevercomesfirst.

Service andparts are available fromBaifaPower or distributorsinyourlocation.

MODEL:JW-C1875400V  |1500rpm  |50Hz

| ENGINESPECIFICATION |  |
| --- | --- |
| Manufacturer /Model | CCECCumminsKTA50-G15 |
| Airintake system | Turbo, Air/Water cooling |
| Fuel system | PT type fuelpump |
| Cylinder arrangement | 16inV |
| Displacement | 50.3L |
| Bore andstroke | 159*159（mm） |
| Compressionratio | 13.9:1 |
| Rated speed | 1500rpm |
| Max. Standbypower atratedspeed | 1657KW |
| Governor type | Electronic |

| Exhaust System |  |
| --- | --- |
| Exhaust gas flow | 303m3/min |
| Exhaust temperature | 601℃ |
| Maxbackpressure | 5kPa |
| Air IntakeSystem |  |
| Maxintakerestriction | 6.23kPa |
| Combustion air flow | 116m3/min |
| Air flowrequired for radiator | 1800m3/min |

MODEL:JW-C1875400V  |1500rpm  |50Hz

| Fuel System |  |  |
| --- | --- | --- |
| Fuelconsumption@100%(StandbyPower)Load | 195g/kWh | 372L/h |
| Fuelconsumption@ 75%(StandbyPower)Load | 198g/kWh | 283L/h |
| Fuelconsumption@ 50%(StandbyPower)Load | 204 g/kWh | 198L/h |

| OilSystem |  |
| --- | --- |
| Total oilcapacity | 204L |
| Oil consumption | ≤4g/kwh |
| Oil sumpcapacity | 148~178L |

| Cooling System |  |
| --- | --- |
| Coolant capacity | 420L |
| Max water temperature | 104℃ |

MODEL:JW-C1875400V  |1500rpm  |50Hz

| ALTERNATORSPECIFICATION |  |
| --- | --- |
| IndustrialalternatorsmeettherequirementsoftherelevantpartsoftheBS5000, VDE0530,NEMAMG1-22,IEC34, CSA 22.2-100 andAS1359. |  |
| Number ofPhase | 3 |
| Connecting Type | 3Phaseand 4 Wires, Ytypeconnecting |
| Number of Bearing | 1 |
| PowerFactor | 0.8 |
| Protection Class | IP23 |
| Altitude | ≤1000m |
| Exciter Type | Brushless exciting |
| InsulationClass/TemperatureRise | H/H |
| TelephoneInfluenceFactor(TIF) | ＜50 |
| THF | ＜2% |
| Alternator Capacity | 1775kVA |
| Alternator Efficiency | 95.9% |

MODEL:JW-C1875400V  |1500rpm  |50Hz

| GENERATINGSETDATA |  |
| --- | --- |
| Relatedrange of voltage setting | ≥±5% |
| Steady-state voltage deviation | ≤±1% |
| Transientvoltagedeviation(100 % suddenpower decrease) | ≤+25% |
| Transient voltage deviation(suddenpowerincrease) | ≤-20% |
| Voltagerecoverytime (100% suddenpowerdecrease) | ≤6S |
| Voltagerecovery time (suddenpowerincrease) | ≤6S |
| Relatedrange of frequency setting | 0-5% adjustable |
| Steady-state frequencyband | ≤1.5% |
| Transientfrequencydeviation(100 % suddenpower decrease) | ≤+12% |
| Transient frequency deviation(suddenpowerincrease) | ≤-10% |
| Frequencyrecoverytime(100 % suddenpower decrease) | ≤5S |
| Frequencyrecovery time (suddenpowerincrease) | ≤5S |

| STANDARDFEATURES |  |  |
| --- | --- | --- |
| Standard auto controlsystem | Exhaust system(includinguntilmuffler) | Documents |
| Oil drainvalve | Startingbatteries (maintenance-free& watering-free) with connective wires | Special tools |

MODEL:JW-C1875400V  |1500rpm  |50Hz

| OPTIONS |  |  |
| --- | --- | --- |
| Daily fueltank | Rainproof type | Remote controlpanel |
| Alternator heater | Soundproof type | Paralleling system |
| Spareparts | Trailer type | Switchbox |
| Automatic transfer switch |  |  |

| DIMENSIONS&WEIGHT |  |
| --- | --- |
|  | Standard Configuration (opentype) |
|  | OverallDimensions: 5800×2200×2800mm |
|  | Weight:11600kg |
|  | SoundproofType (standard 20’ftHQcontainer) |
|  | OverallDimensions: 6058×2438×2896mm |
|  | Weight:16600kg |

Specifications are subject to changewithoutnotice.

SICHUAN JIWEICHENG ELECTRIC POWER EQUIPMENT CO., LTD

WEBSITE:WWW.SCJIWEI.COM

ADDRESS：Building 7, Chengnan Tianfu Wisdom Park,

Pengshan District, Meishan City, Sichuan Province